## Slide 1
Specifications and parameters
Battery type: Organic Flow Battery, 13-ft
Power rating: 25 kW
Capacity rating: 150 kWh
Investment cost: €60000 (€400/kWh | Includes: battery, PCS, BoP. Excludes: Installation cost)
Pilot lifetime guarantee: >5000 cycles or 7 years with >70% remaining capacity
Round-trip efficiency: 72.2% AC-AC
Operating SOC window: 100%
Electricity demand data: Jan 2024 - Dec 2024
Electricity cost & FCR data: Jan 2024 - Dec 2025
Additional Information
Net hourly demand data was provided together with hourly PV production for 2024 and 2025. Based on this information, gross hourly demand data was calculated with the help of hourly means.
13-ft Organic flow battery
Fire-proof, sustainable & low lifecycle cost
7.1 – 11.1 years
Payback time of the battery
With Peak Shaving, Arbitrage, and Ancillary Market revenues
Revenue Share by type*
Arbitrage 82.7%
info@rivus-batteries.com 0046 763 01 29 16 www.rivus-batteries.com
Increase in self-sufficiency
% of on-site electricity demand met by PV with “self-sufficiency” objective
1.9x
Simulation Findings Sheet – Gödestadsvägen
We simulated how a 150 kWh, 25 kW battery + PV affects your electricity cost and grid fees based on your 2024 data. Key outcomes:
Peak Shaving 6.4%
Ancillary Market Revenue 10.9%

## Slide 2
Findings – Gödestadsvägen Average annual demand: 64.2 MWh Total PV generation in period: 13.7 MWh |  |  |  |  |  | 
 | 2024 |  |  | 2025 |  | 
Simulation / ​​Use-case | Baseline | Battery I (150 kWh, 25 kW) | Battery II (150 kWh, 25 kW) | Baseline | Battery I (150 kWh, 25 kW) | Battery II (150 kWh, 25 kW)
 | PV installed | Peak Shaving, Arbitrage, Ancillary Market revenues | Self-sufficiency objective and Peak Shaving, Arbitrage, Ancillary Market revenues | PV installed | Peak Shaving, Arbitrage, Ancillary Market revenues | Self-sufficiency objective and Peak Shaving, Arbitrage, Ancillary Market revenues
Total investments PV or Battery (B) | PV: €0 B: €0 | PV: €0 B: €60000 | PV: €0 B: €60000 | PV: €0 B: €0 | PV: €0 B: €60000 | PV: €0 B: €60000
Average electricity cost / year | €0.038/kWh | €0.0286/kWh | €0.0349/kWh | €0.058/kWh | €0.0306/kWh | €0.0528/kWh
Total annual electricity cost | €2409.0 | €1834.0 | €2237.0 | €3739.0 | €1960.0 | €3383.0
Annual ancillary market revenue | - | €7392.0 | €6748.0 | - | €4267.0 | €4605.0
Grid fees saved | - | €453.0 | €459.0 | - | €375.0 | €444.0
Annual savings from the Battery (B) & PV | - PV: €272.0 | B: €8420.0 PV: €272.0 | B: €7378.0 PV: €272.0 | - PV: €432.0 | B: €6422.0 PV: €432.0 | B: €5405.0 PV: €432.0
Payback time Battery | - | 7.1 years | 8.1 years | - | 9.3 years | 11.1 years
Self-sufficiency % of on-site electricity demand met by PV | 10.6% | 10.7% | 20.0% | 10.7% | 11.1% | 20.5%
Equivalent Full Cycles per year | - | 60.8 cycles | 57.6 cycles | - | 139.0 cycles | 52.9 cycles
Time inside SoC 20%-80% | - | 75.1% | 77.4% | - | 62.3% | 80.8%
Total MWh charged /discharged | - | 9.1 MWh | 8.6 MWh | - | 20.8 MWh | 7.9 MWh
info@rivus-batteries.com 0046 763 01 29 16 www.rivus-batteries.com

## Slide 3
Simulation results in more detail
We invite those interested to explore the batteries’ behaviour. How? Click on this link here and download the file you’d like to see to a good location on your computer. From there, open the HTML document (for example in your web browser) and you’ll be able to zoom in and check out what happens during every hour of the day!
The HTML will look something like the figure below:
Electricity price (yellow) and the battery’s state of charge (pink)
Amount of energy charged (black) and discharged (blue)
Bid quantity of ancillary services for the various capacity markets
Key assumptions and parameters
Electricity cost Day-ahead prices SE3, repeated over lifetime
Ancillary market revenue Participation in FCR-N,FCR-D up/down, mimer.svk.se
Grid fees costs saved Effect of peak shaving on demand charges (4 €/kW)
Operating SOC window: 100%
IRR/NPV N/A – not used in the simulation
If you’d like to move forward, we’d be happy to outline the next steps! Just let us know if you have any questions. We are ready to deliver the 25 kW, 150-kWh battery in 2027.
info@rivus-batteries.com 0046 763 01 29 16 www.rivus-batteries.com